## Estimator
kV | Type of Conductor | Conductors Per Phase | Shield | Geometry | Amps | MVA | R / Mile | X / Mile | B / Mile | R0 / Mile | X0 / Mile | Mileage | R | X | B | R0 | X0
69 | 336.4 26/7 ACSR LINNET | 1 | 3/8 | delta | 540 | 64.5362 | 0.00687 | 0.01717 | 0.00025 | 0.01459 | 0.05392 | 1 | 0.00687 | 0.01717 | 0.00025 | 0.01459 | 0.05392
69 | 336.4 26/7 ACSR LINNET | 1 | 7#8 | delta | 540 | 64.5362 | 0.00687 | 0.01717 | 0.00025 | 0.01664 | 0.05052 | 1 | 0.00687 | 0.01717 | 0.00025 | 0.01664 | 0.05052
69 | 336.4 26/7 ACSR LINNET | 1 | OPGW | delta | 540 | 64.5362 | 0.00687 | 0.01716 | 0.00025 | 0.01336 | 0.04249 | 1 | 0.00687 | 0.01716 | 0.00025 | 0.01336 | 0.04249
69 | 336.4 26/7 ACSR LINNET | 1 | 3/8 | H | 540 | 64.5362 | 0.00687 | 0.01682 | 0.00025 | 0.01674 | 0.05217 | 1 | 0.00687 | 0.01682 | 0.00025 | 0.01674 | 0.05217
69 | 336.4 26/7 ACSR LINNET | 1 | 7#8 | H | 540 | 64.5362 | 0.00688 | 0.01682 | 0.00025 | 0.01936 | 0.04512 | 1 | 0.00688 | 0.01682 | 0.00025 | 0.01936 | 0.04512
69 | 336.4 26/7 ACSR LINNET | 1 | OPGW | H | 540 | 64.5362 | 0.00689 | 0.01679 | 0.00025 | 0.01282 | 0.03453 | 1 | 0.00689 | 0.01679 | 0.00025 | 0.01282 | 0.03453
69 | 336.4 26/7 ACSR LINNET | 1 | 3/8 | vertical | 540 | 64.5362 | 0.00688 | 0.01677 | 0.00026 | 0.01463 | 0.0547 | 1 | 0.00688 | 0.01677 | 0.00026 | 0.01463 | 0.0547
69 | 336.4 26/7 ACSR LINNET | 1 | 7#8 | vertical | 540 | 64.5362 | 0.00689 | 0.01677 | 0.00026 | 0.01672 | 0.05124 | 1 | 0.00689 | 0.01677 | 0.00026 | 0.01672 | 0.05124
69 | 336.4 26/7 ACSR LINNET | 1 | OPGW | vertical | 540 | 64.5362 | 0.00689 | 0.01673 | 0.00026 | 0.01342 | 0.04297 | 1 | 0.00689 | 0.01673 | 0.00026 | 0.01342 | 0.04297
69 | 795.0 26/7 ACSR DRAKE | 1 | 3/8 | delta | 933 | 111.5042 | 0.00292 | 0.01608 | 0.00027 | 0.01263 | 0.05283 | 1 | 0.00292 | 0.01608 | 0.00027 | 0.01263 | 0.05283
69 | 795.0 26/7 ACSR DRAKE | 1 | 7#8 | delta | 933 | 111.5042 | 0.00293 | 0.01607 | 0.00027 | 0.01267 | 0.04945 | 1 | 0.00293 | 0.01607 | 0.00027 | 0.01267 | 0.04945
69 | 795.0 26/7 ACSR DRAKE | 1 | OPGW | delta | 933 | 111.5042 | 0.00293 | 0.01606 | 0.00027 | 0.0094 | 0.04145 | 1 | 0.00293 | 0.01606 | 0.00027 | 0.0094 | 0.04145
69 | 795.0 26/7 ACSR DRAKE | 1 | 3/8 | H | 933 | 111.5042 | 0.00292 | 0.01573 | 0.00027 | 0.01276 | 0.05109 | 1 | 0.00292 | 0.01573 | 0.00027 | 0.01276 | 0.05109
69 | 795.0 26/7 ACSR DRAKE | 1 | 7#8 | H | 933 | 111.5042 | 0.00293 | 0.01572 | 0.00027 | 0.01536 | 0.04407 | 1 | 0.00293 | 0.01572 | 0.00027 | 0.01536 | 0.04407
69 | 795.0 26/7 ACSR DRAKE | 1 | OPGW | H | 933 | 111.5042 | 0.00294 | 0.0157 | 0.00027 | 0.00885 | 0.03356 | 1 | 0.00294 | 0.0157 | 0.00027 | 0.00885 | 0.03356
69 | 795.0 26/7 ACSR DRAKE | 1 | 3/8 | vertical | 933 | 111.5042 | 0.00293 | 0.01568 | 0.00027 | 0.01068 | 0.0536 | 1 | 0.00293 | 0.01568 | 0.00027 | 0.01068 | 0.0536
69 | 795.0 26/7 ACSR DRAKE | 1 | 7#8 | vertical | 933 | 111.5042 | 0.00294 | 0.01567 | 0.00027 | 0.01275 | 0.05017 | 1 | 0.00294 | 0.01567 | 0.00027 | 0.01275 | 0.05017
69 | 795.0 26/7 ACSR DRAKE | 1 | OPGW | vertical | 933 | 111.5042 | 0.00294 | 0.01564 | 0.00027 | 0.00946 | 0.04195 | 1 | 0.00294 | 0.01564 | 0.00027 | 0.00946 | 0.04195
138 | 477.0 26/7 ACSR HAWK | 1 | OPGW | H | 672 | 160.6235 | 0.00122 | 0.00409 | 0.00105 | 0.00269 | 0.00856 | 1 | 0.00122 | 0.00409 | 0.00105 | 0.00269 | 0.00856
138 | 477.0 26/7 ACSR HAWK | 1 | OPGW | DBL ckt | 672 | 160.6235 | 0.00122 | 0.00407 | 0.00106 | 0.00254 | 0.00948 | 1 | 0.00122 | 0.00407 | 0.00106 | 0.00254 | 0.00948
138 | 477.0 26/7 ACSR HAWK | 1 | OPGW | delta | 672 | 160.6235 | 0.00121 | 0.00418 | 0.00102 | 0.00283 | 0.01053 | 1 | 0.00121 | 0.00418 | 0.00102 | 0.00283 | 0.01053
138 | 477.0 26/7 ACSR HAWK | 1 | OPGW | vertical | 672 | 160.6235 | 0.00122 | 0.00407 | 0.00105 | 0.00285 | 0.01066 | 1 | 0.00122 | 0.00407 | 0.00105 | 0.00285 | 0.01066
138 | 477.0 26/7 ACSR HAWK | 1 | 7#8 | H | 672 | 160.6235 | 0.00122 | 0.00409 | 0.00105 | 0.00432 | 0.01119 | 1 | 0.00122 | 0.00409 | 0.00105 | 0.00432 | 0.01119
138 | 477.0 26/7 ACSR HAWK | 1 | 7#8 | DBL ckt | 672 | 160.6235 | 0.00122 | 0.00408 | 0.00106 | 0.00399 | 0.01157 | 1 | 0.00122 | 0.00408 | 0.00106 | 0.00399 | 0.01157
138 | 477.0 26/7 ACSR HAWK | 1 | 7#8 | delta | 672 | 160.6235 | 0.00121 | 0.00418 | 0.00102 | 0.00365 | 0.01253 | 1 | 0.00121 | 0.00418 | 0.00102 | 0.00365 | 0.01253
138 | 477.0 26/7 ACSR HAWK | 1 | 7#8 | vertical | 672 | 160.6235 | 0.00122 | 0.00408 | 0.00105 | 0.00367 | 0.01271 | 1 | 0.00122 | 0.00408 | 0.00105 | 0.00367 | 0.01271
138 | 477.0 26/7 ACSR HAWK | 1 | 3/8 | H | 672 | 160.6235 | 0.00121 | 0.0041 | 0.00105 | 0.00367 | 0.01294 | 1 | 0.00121 | 0.0041 | 0.00105 | 0.00367 | 0.01294
138 | 477.0 26/7 ACSR HAWK | 1 | 3/8 | DBL ckt | 672 | 160.6235 | 0.00122 | 0.00408 | 0.00106 | 0.0035 | 0.0131 | 1 | 0.00122 | 0.00408 | 0.00106 | 0.0035 | 0.0131
138 | 477.0 26/7 ACSR HAWK | 1 | 3/8 | delta | 672 | 160.6235 | 0.00121 | 0.00418 | 0.00102 | 0.00314 | 0.01337 | 1 | 0.00121 | 0.00418 | 0.00102 | 0.00314 | 0.01337
138 | 477.0 26/7 ACSR HAWK | 1 | 3/8 | vertical | 672 | 160.6235 | 0.00122 | 0.00408 | 0.00105 | 0.00315 | 0.01357 | 1 | 0.00122 | 0.00408 | 0.00105 | 0.00315 | 0.01357
138 | 795.0 26/7 ACSR DRAKE | 1 | OPGW | H | 933 | 223.0085 | 0.00073 | 0.00392 | 0.00109 | 0.00221 | 0.00839 | 1 | 0.00073 | 0.00392 | 0.00109 | 0.00221 | 0.00839
138 | 795.0 26/7 ACSR DRAKE | 1 | 7#8 | H | 933 | 223.0085 | 0.00073 | 0.00393 | 0.00109 | 0.00384 | 0.01102 | 1 | 0.00073 | 0.00393 | 0.00109 | 0.00384 | 0.01102
138 | 795.0 26/7 ACSR DRAKE | 1 | 7#8 | DBL ckt | 933 | 223.0085 | 0.00074 | 0.00392 | 0.0011 | 0.00351 | 0.01141 | 1 | 0.00074 | 0.00392 | 0.0011 | 0.00351 | 0.01141
138 | 795.0 26/7 ACSR DRAKE | 1 | 7#8 | delta | 933 | 223.0085 | 0.00073 | 0.00402 | 0.00106 | 0.00317 | 0.01236 | 1 | 0.00073 | 0.00402 | 0.00106 | 0.00317 | 0.01236
138 | 795.0 26/7 ACSR DRAKE | 1 | 7#8 | vertical | 933 | 223.0085 | 0.00073 | 0.00392 | 0.0011 | 0.00319 | 0.01254 | 1 | 0.00073 | 0.00392 | 0.0011 | 0.00319 | 0.01254
138 | 795.0 26/7 ACSR DRAKE | 1 | 3/8 | H | 933 | 223.0085 | 0.00073 | 0.00393 | 0.00109 | 0.00319 | 0.01277 | 1 | 0.00073 | 0.00393 | 0.00109 | 0.00319 | 0.01277
138 | 795.0 26/7 ACSR DRAKE | 1 | 3/8 | DBL ckt | 933 | 223.0085 | 0.00073 | 0.00392 | 0.0011 | 0.00302 | 0.01293 | 1 | 0.00073 | 0.00392 | 0.0011 | 0.00302 | 0.01293
138 | 795.0 26/7 ACSR DRAKE | 1 | 3/8 | delta | 933 | 223.0085 | 0.00073 | 0.00402 | 0.00106 | 0.00266 | 0.01321 | 1 | 0.00073 | 0.00402 | 0.00106 | 0.00266 | 0.01321
138 | 795.0 26/7 ACSR DRAKE | 1 | 3/8 | vertical | 933 | 223.0085 | 0.00073 | 0.00392 | 0.0011 | 0.00267 | 0.0134 | 1 | 0.00073 | 0.00392 | 0.0011 | 0.00267 | 0.0134
138 | 795.0 26/7 ACSS/AW DRAKE | 1 | OPGW | H | 933 | 223.0085 | 0.0007 | 0.00392 | 0.00109 | 0.00218 | 0.00838 | 1 | 0.0007 | 0.00392 | 0.00109 | 0.00218 | 0.00838
138 | 795.0 26/7 ACSS/AW DRAKE | 1 | OPGW | DBL ckt | 933 | 223.0085 | 0.0007 | 0.00391 | 0.0011 | 0.00202 | 0.0093 | 1 | 0.0007 | 0.00391 | 0.0011 | 0.00202 | 0.0093
138 | 795.0 26/7 ACSS/AW DRAKE | 1 | OPGW | delta | 933 | 223.0085 | 0.00069 | 0.00402 | 0.00106 | 0.00231 | 0.01036 | 1 | 0.00069 | 0.00402 | 0.00106 | 0.00231 | 0.01036
138 | 795.0 26/7 ACSS/AW DRAKE | 1 | OPGW | vertical | 933 | 223.0085 | 0.0007 | 0.00391 | 0.0011 | 0.00233 | 0.01048 | 1 | 0.0007 | 0.00391 | 0.0011 | 0.00233 | 0.01048
138 | 795.0 26/7 ACSS/AW DRAKE | 1 | 7#8 | H | 933 | 223.0085 | 0.00069 | 0.00393 | 0.00109 | 0.00381 | 0.01101 | 1 | 0.00069 | 0.00393 | 0.00109 | 0.00381 | 0.01101
138 | 795.0 26/7 ACSS/AW DRAKE | 1 | 7#8 | DBL ckt | 933 | 223.0085 | 0.0007 | 0.00392 | 0.0011 | 0.00348 | 0.0114 | 1 | 0.0007 | 0.00392 | 0.0011 | 0.00348 | 0.0114
138 | 795.0 26/7 ACSS/AW DRAKE | 1 | 7#8 | delta | 933 | 223.0085 | 0.00069 | 0.00402 | 0.00106 | 0.00313 | 0.01236 | 1 | 0.00069 | 0.00402 | 0.00106 | 0.00313 | 0.01236
138 | 795.0 26/7 ACSS/AW DRAKE | 1 | 7#8 | vertical | 933 | 223.0085 | 0.0007 | 0.00392 | 0.0011 | 0.00315 | 0.01254 | 1 | 0.0007 | 0.00392 | 0.0011 | 0.00315 | 0.01254
138 | 795.0 26/7 ACSS/AW DRAKE | 1 | 3/8 | H | 933 | 223.0085 | 0.00069 | 0.00393 | 0.00109 | 0.00316 | 0.01277 | 1 | 0.00069 | 0.00393 | 0.00109 | 0.00316 | 0.01277
138 | 795.0 26/7 ACSS/AW DRAKE | 1 | 3/8 | DBL ckt | 933 | 223.0085 | 0.0007 | 0.00392 | 0.0011 | 0.00298 | 0.01293 | 1 | 0.0007 | 0.00392 | 0.0011 | 0.00298 | 0.01293
138 | 795.0 26/7 ACSS/AW DRAKE | 1 | 3/8 | delta | 933 | 223.0085 | 0.00069 | 0.00402 | 0.00106 | 0.00262 | 0.01321 | 1 | 0.00069 | 0.00402 | 0.00106 | 0.00262 | 0.01321
138 | 795.0 26/7 ACSS/AW DRAKE | 1 | 3/8 | vertical | 933 | 223.0085 | 0.00069 | 0.00392 | 0.0011 | 0.00263 | 0.0134 | 1 | 0.00069 | 0.00392 | 0.0011 | 0.00263 | 0.0134
138 | 795.0 26/7 ACSR DRAKE | 1 | OPGW | DBL ckt | 933 | 223.0085 | 0.00073 | 0.00391 | 0.0011 | 0.00206 | 0.00931 | 1 | 0.00073 | 0.00391 | 0.0011 | 0.00206 | 0.00931
138 | 795.0 26/7 ACSR DRAKE | 1 | OPGW | delta | 933 | 223.0085 | 0.00073 | 0.00402 | 0.00106 | 0.00235 | 0.01036 | 1 | 0.00073 | 0.00402 | 0.00106 | 0.00235 | 0.01036
138 | 795.0 26/7 ACSR DRAKE | 1 | OPGW | vertical | 933 | 223.0085 | 0.00073 | 0.00391 | 0.0011 | 0.00236 | 0.01049 | 1 | 0.00073 | 0.00391 | 0.0011 | 0.00236 | 0.01049
138 | 477.0 26/7 ACSR HAWK | 2 | OPGW | H | 1344 | 321.2469 | 0.00061 | 0.00283 | 0.00151 | 0.00209 | 0.0073 | 1 | 0.00061 | 0.00283 | 0.00151 | 0.00209 | 0.0073
138 | 477.0 26/7 ACSR HAWK | 2 | OPGW | DBL ckt | 1344 | 321.2469 | 0.00061 | 0.00281 | 0.00153 | 0.00194 | 0.00822 | 1 | 0.00061 | 0.00281 | 0.00153 | 0.00194 | 0.00822
138 | 477.0 26/7 ACSR HAWK | 2 | OPGW | delta | 1344 | 321.2469 | 0.00061 | 0.00292 | 0.00145 | 0.00223 | 0.00927 | 1 | 0.00061 | 0.00292 | 0.00145 | 0.00223 | 0.00927
138 | 477.0 26/7 ACSR HAWK | 2 | OPGW | vertical | 1344 | 321.2469 | 0.00061 | 0.00281 | 0.00152 | 0.00224 | 0.0094 | 1 | 0.00061 | 0.00281 | 0.00152 | 0.00224 | 0.0094
138 | 477.0 26/7 ACSR HAWK | 2 | 7#8 | H | 1344 | 321.2469 | 0.00061 | 0.00284 | 0.00372 | 0.00372 | 0.00993 | 1 | 0.00061 | 0.00284 | 0.00372 | 0.00372 | 0.00993
138 | 477.0 26/7 ACSR HAWK | 2 | 7#8 | DBL ckt | 1344 | 321.2469 | 0.00061 | 0.00282 | 0.00153 | 0.00339 | 0.01032 | 1 | 0.00061 | 0.00282 | 0.00153 | 0.00339 | 0.01032
138 | 477.0 26/7 ACSR HAWK | 2 | 7#8 | delta | 1344 | 321.2469 | 0.00061 | 0.00292 | 0.00145 | 0.00304 | 0.01127 | 1 | 0.00061 | 0.00292 | 0.00145 | 0.00304 | 0.01127
138 | 477.0 26/7 ACSR HAWK | 2 | 7#8 | vertical | 1344 | 321.2469 | 0.00061 | 0.00282 | 0.00152 | 0.00306 | 0.01145 | 1 | 0.00061 | 0.00282 | 0.00152 | 0.00306 | 0.01145
138 | 477.0 26/7 ACSR HAWK | 2 | 3/8 | H | 1344 | 321.2469 | 0.00061 | 0.00284 | 0.00151 | 0.00307 | 0.01168 | 1 | 0.00061 | 0.00284 | 0.00151 | 0.00307 | 0.01168
138 | 477.0 26/7 ACSR HAWK | 2 | 3/8 | DBL ckt | 1344 | 321.2469 | 0.00061 | 0.00282 | 0.00153 | 0.00289 | 0.01184 | 1 | 0.00061 | 0.00282 | 0.00153 | 0.00289 | 0.01184
138 | 477.0 26/7 ACSR HAWK | 2 | 3/8 | delta | 1344 | 321.2469 | 0.00061 | 0.00293 | 0.00145 | 0.00253 | 0.01212 | 1 | 0.00061 | 0.00293 | 0.00145 | 0.00253 | 0.01212
138 | 477.0 26/7 ACSR HAWK | 2 | 3/8 | vertical | 1344 | 321.2469 | 0.00061 | 0.00282 | 0.00152 | 0.00254 | 0.01231 | 1 | 0.00061 | 0.00282 | 0.00152 | 0.00254 | 0.01231
138 | 959.6 22/7 ACSS/ TW SUWANNEE | 1 | OPGW | H | 1595 | 381.2417 | 0.0006 | 0.00393 | 0.00109 | 0.00208 | 0.00838 | 1 | 0.0006 | 0.00393 | 0.00109 | 0.00208 | 0.00838
138 | 959.6 22/7 ACSS/ TW SUWANNEE | 1 | OPGW | DBL ckt | 1595 | 381.2417 | 0.00059 | 0.00391 | 0.0011 | 0.00192 | 0.0093 | 1 | 0.00059 | 0.00391 | 0.0011 | 0.00192 | 0.0093
138 | 959.6 22/7 ACSS/ TW SUWANNEE | 1 | OPGW | delta | 1595 | 381.2417 | 0.00059 | 0.00402 | 0.00106 | 0.00221 | 0.01036 | 1 | 0.00059 | 0.00402 | 0.00106 | 0.00221 | 0.01036
138 | 959.6 22/7 ACSS/ TW SUWANNEE | 1 | OPGW | vertical | 1595 | 381.2417 | 0.00059 | 0.00391 | 0.0011 | 0.00223 | 0.01048 | 1 | 0.00059 | 0.00391 | 0.0011 | 0.00223 | 0.01048
138 | 959.6 22/7 ACSS/ TW SUWANNEE | 1 | 7#8 | H | 1595 | 381.2417 | 0.00059 | 0.00393 | 0.00109 | 0.00371 | 0.01102 | 1 | 0.00059 | 0.00393 | 0.00109 | 0.00371 | 0.01102
138 | 959.6 22/7 ACSS/ TW SUWANNEE | 1 | 7#8 | DBL ckt | 1595 | 381.2417 | 0.0006 | 0.00392 | 0.0011 | 0.00337 | 0.01141 | 1 | 0.0006 | 0.00392 | 0.0011 | 0.00337 | 0.01141
138 | 959.6 22/7 ACSS/ TW SUWANNEE | 1 | 7#8 | delta | 1595 | 381.2417 | 0.00059 | 0.00402 | 0.00106 | 0.00303 | 0.01236 | 1 | 0.00059 | 0.00402 | 0.00106 | 0.00303 | 0.01236
138 | 959.6 22/7 ACSS/ TW SUWANNEE | 1 | 7#8 | vertical | 1595 | 381.2417 | 0.00059 | 0.00392 | 0.0011 | 0.00305 | 0.01254 | 1 | 0.00059 | 0.00392 | 0.0011 | 0.00305 | 0.01254
138 | 959.6 22/7 ACSS/ TW SUWANNEE | 1 | 3/8 | H | 1595 | 381.2417 | 0.00059 | 0.00394 | 0.00109 | 0.00305 | 0.01278 | 1 | 0.00059 | 0.00394 | 0.00109 | 0.00305 | 0.01278
138 | 959.6 22/7 ACSS/ TW SUWANNEE | 1 | 3/8 | DBL ckt | 1595 | 381.2417 | 0.00059 | 0.00392 | 0.0011 | 0.00288 | 0.01294 | 1 | 0.00059 | 0.00392 | 0.0011 | 0.00288 | 0.01294
138 | 959.6 22/7 ACSS/ TW SUWANNEE | 1 | 3/8 | delta | 1595 | 381.2417 | 0.00059 | 0.00402 | 0.00106 | 0.00252 | 0.01321 | 1 | 0.00059 | 0.00402 | 0.00106 | 0.00252 | 0.01321
138 | 959.6 22/7 ACSS/ TW SUWANNEE | 1 | 3/8 | vertical | 1595 | 381.2417 | 0.00059 | 0.00392 | 0.0011 | 0.00253 | 0.01341 | 1 | 0.00059 | 0.00392 | 0.0011 | 0.00253 | 0.01341
138 | 795.0 26/7 ACSR DRAKE | 2 | OPGW | H | 1866 | 446.0169 | 0.00037 | 0.00275 | 0.00156 | 0.00185 | 0.00721 | 1 | 0.00037 | 0.00275 | 0.00156 | 0.00185 | 0.00721
138 | 795.0 26/7 ACSR DRAKE | 2 | OPGW | DBL ckt | 1866 | 446.0169 | 0.00037 | 0.00273 | 0.00158 | 0.0017 | 0.00813 | 1 | 0.00037 | 0.00273 | 0.00158 | 0.0017 | 0.00813
138 | 795.0 26/7 ACSR DRAKE | 2 | OPGW | delta | 1866 | 446.0169 | 0.00037 | 0.00284 | 0.00149 | 0.00199 | 0.00919 | 1 | 0.00037 | 0.00284 | 0.00149 | 0.00199 | 0.00919
138 | 795.0 26/7 ACSR DRAKE | 2 | OPGW | vertical | 1866 | 446.0169 | 0.00037 | 0.00273 | 0.00157 | 0.002 | 0.00931 | 1 | 0.00037 | 0.00273 | 0.00157 | 0.002 | 0.00931
138 | 795.0 26/7 ACSR DRAKE | 2 | 7#8 | H | 1866 | 446.0169 | 0.00037 | 0.00276 | 0.00155 | 0.00348 | 0.00984 | 1 | 0.00037 | 0.00276 | 0.00155 | 0.00348 | 0.00984
138 | 795.0 26/7 ACSR DRAKE | 2 | 7#8 | DBL ckt | 1866 | 446.0169 | 0.00037 | 0.00274 | 0.00158 | 0.00315 | 0.01023 | 1 | 0.00037 | 0.00274 | 0.00158 | 0.00315 | 0.01023
138 | 795.0 26/7 ACSR DRAKE | 2 | 7#8 | delta | 1866 | 446.0169 | 0.00037 | 0.00284 | 0.00149 | 0.0028 | 0.01119 | 1 | 0.00037 | 0.00284 | 0.00149 | 0.0028 | 0.01119
138 | 795.0 26/7 ACSR DRAKE | 2 | 7#8 | vertical | 1866 | 446.0169 | 0.00037 | 0.00274 | 0.00157 | 0.00282 | 0.01137 | 1 | 0.00037 | 0.00274 | 0.00157 | 0.00282 | 0.01137
138 | 795.0 26/7 ACSR DRAKE | 2 | 3/8 | H | 1866 | 446.0169 | 0.00037 | 0.00276 | 0.00156 | 0.00283 | 0.0116 | 1 | 0.00037 | 0.00276 | 0.00156 | 0.00283 | 0.0116
138 | 795.0 26/7 ACSR DRAKE | 2 | 3/8 | DBL ckt | 1866 | 446.0169 | 0.00037 | 0.00274 | 0.00158 | 0.00265 | 0.01176 | 1 | 0.00037 | 0.00274 | 0.00158 | 0.00265 | 0.01176
138 | 795.0 26/7 ACSR DRAKE | 2 | 3/8 | delta | 1866 | 446.0169 | 0.00037 | 0.00284 | 0.00149 | 0.00229 | 0.01203 | 1 | 0.00037 | 0.00284 | 0.00149 | 0.00229 | 0.01203
138 | 795.0 26/7 ACSR DRAKE | 2 | 3/8 | vertical | 1866 | 446.0169 | 0.00037 | 0.00274 | 0.00157 | 0.0023 | 0.01223 | 1 | 0.00037 | 0.00274 | 0.00157 | 0.0023 | 0.01223
138 | 795.0 26/7 ACSS/AW DRAKE | 2 | OPGW | H | 1866 | 446.0169 | 0.00035 | 0.00275 | 0.00156 | 0.00183 | 0.0072 | 1 | 0.00035 | 0.00275 | 0.00156 | 0.00183 | 0.0072
138 | 795.0 26/7 ACSS/AW DRAKE | 2 | OPGW | DBL ckt | 1866 | 446.0169 | 0.00035 | 0.00273 | 0.00158 | 0.00168 | 0.00812 | 1 | 0.00035 | 0.00273 | 0.00158 | 0.00168 | 0.00812
138 | 795.0 26/7 ACSS/AW DRAKE | 2 | OPGW | delta | 1866 | 446.0169 | 0.00035 | 0.00284 | 0.00149 | 0.00197 | 0.00918 | 1 | 0.00035 | 0.00284 | 0.00149 | 0.00197 | 0.00918
138 | 795.0 26/7 ACSS/AW DRAKE | 2 | OPGW | vertical | 1866 | 446.0169 | 0.00035 | 0.00273 | 0.00157 | 0.00198 | 0.00931 | 1 | 0.00035 | 0.00273 | 0.00157 | 0.00198 | 0.00931
138 | 795.0 26/7 ACSS/AW DRAKE | 2 | 7#8 | H | 1866 | 446.0169 | 0.00035 | 0.00276 | 0.00155 | 0.00346 | 0.00984 | 1 | 0.00035 | 0.00276 | 0.00155 | 0.00346 | 0.00984
138 | 795.0 26/7 ACSS/AW DRAKE | 2 | 7#8 | DBL ckt | 1866 | 446.0169 | 0.00035 | 0.00274 | 0.00158 | 0.00313 | 0.01023 | 1 | 0.00035 | 0.00274 | 0.00158 | 0.00313 | 0.01023
138 | 795.0 26/7 ACSS/AW DRAKE | 2 | 7#8 | delta | 1866 | 446.0169 | 0.00035 | 0.00284 | 0.00149 | 0.00279 | 0.01118 | 1 | 0.00035 | 0.00284 | 0.00149 | 0.00279 | 0.01118
138 | 795.0 26/7 ACSS/AW DRAKE | 2 | 7#8 | vertical | 1866 | 446.0169 | 0.00035 | 0.00274 | 0.00157 | 0.00281 | 0.01137 | 1 | 0.00035 | 0.00274 | 0.00157 | 0.00281 | 0.01137
138 | 795.0 26/7 ACSS/AW DRAKE | 2 | 3/8 | H | 1866 | 446.0169 | 0.00035 | 0.00276 | 0.00156 | 0.00281 | 0.01159 | 1 | 0.00035 | 0.00276 | 0.00156 | 0.00281 | 0.01159
138 | 795.0 26/7 ACSS/AW DRAKE | 2 | 3/8 | DBL ckt | 1866 | 446.0169 | 0.00035 | 0.00274 | 0.00158 | 0.00263 | 0.01176 | 1 | 0.00035 | 0.00274 | 0.00158 | 0.00263 | 0.01176
138 | 795.0 26/7 ACSS/AW DRAKE | 2 | 3/8 | delta | 1866 | 446.0169 | 0.00035 | 0.00284 | 0.00149 | 0.00228 | 0.01203 | 1 | 0.00035 | 0.00284 | 0.00149 | 0.00228 | 0.01203
138 | 795.0 26/7 ACSS/AW DRAKE | 2 | 3/8 | vertical | 1866 | 446.0169 | 0.00035 | 0.00274 | 0.00157 | 0.00228 | 0.01223 | 1 | 0.00035 | 0.00274 | 0.00157 | 0.00228 | 0.01223
138 | 1433.6 39/19 ACSS/TW MERRIMACK | 1 | OPGW | H | 2000 | 478.046 | 0.00041 | 0.00381 | 0.00113 | 0.00187 | 0.00838 | 1 | 0.00041 | 0.00381 | 0.00113 | 0.00187 | 0.00838
138 | 1433.6 39/19 ACSS/TW MERRIMACK | 1 | OPGW | DBL ckt | 2000 | 478.046 | 0.00041 | 0.00379 | 0.00114 | 0.00173 | 0.00927 | 1 | 0.00041 | 0.00379 | 0.00114 | 0.00173 | 0.00927
138 | 1433.6 39/19 ACSS/TW MERRIMACK | 1 | OPGW | delta | 2000 | 478.046 | 0.00041 | 0.0039 | 0.0011 | 0.00201 | 0.0103 | 6.95 | 0.0028495 | 0.027105 | 0.007645 | 0.01397 | 0.071585
138 | 1433.6 39/19 ACSS/TW MERRIMACK | 1 | OPGW | vertical | 2000 | 478.046 | 0.00041 | 0.00379 | 0.00113 | 0.00203 | 0.01043 | 1 | 0.00041 | 0.00379 | 0.00113 | 0.00203 | 0.01043
138 | 1433.6 39/19 ACSS/TW MERRIMACK | 1 | 7#8 | H | 2000 | 478.046 | 0.00041 | 0.00381 | 0.00113 | 0.00348 | 0.01095 | 1 | 0.00041 | 0.00381 | 0.00113 | 0.00348 | 0.01095
138 | 1433.6 39/19 ACSS/TW MERRIMACK | 1 | 7#8 | DBL ckt | 2000 | 478.046 | 0.00041 | 0.0038 | 0.00114 | 0.00316 | 0.01133 | 1 | 0.00041 | 0.0038 | 0.00114 | 0.00316 | 0.01133
138 | 1433.6 39/19 ACSS/TW MERRIMACK | 1 | 7#8 | delta | 2000 | 478.046 | 0.00041 | 0.0039 | 0.0011 | 0.00282 | 0.01226 | 1 | 0.00041 | 0.0039 | 0.0011 | 0.00282 | 0.01226
138 | 1433.6 39/19 ACSS/TW MERRIMACK | 1 | 7#8 | vertical | 2000 | 478.046 | 0.00041 | 0.0038 | 0.00113 | 0.00284 | 0.01245 | 1 | 0.00041 | 0.0038 | 0.00113 | 0.00284 | 0.01245
138 | 1433.6 39/19 ACSS/TW MERRIMACK | 1 | 3/8 | H | 2000 | 478.046 | 0.00041 | 0.00382 | 0.00113 | 0.00284 | 0.01267 | 1 | 0.00041 | 0.00382 | 0.00113 | 0.00284 | 0.01267
138 | 1433.6 39/19 ACSS/TW MERRIMACK | 1 | 3/8 | DBL ckt | 2000 | 478.046 | 0.00041 | 0.0038 | 0.00114 | 0.00268 | 0.01283 | 1 | 0.00041 | 0.0038 | 0.00114 | 0.00268 | 0.01283
138 | 1433.6 39/19 ACSS/TW MERRIMACK | 1 | 3/8 | delta | 2000 | 478.046 | 0.00041 | 0.0039 | 0.0011 | 0.00233 | 0.0131 | 1 | 0.00041 | 0.0039 | 0.0011 | 0.00233 | 0.0131
138 | 1433.6 39/19 ACSS/TW MERRIMACK | 1 | 3/8 | vertical | 2000 | 478.046 | 0.00041 | 0.0038 | 0.00113 | 0.00233 | 0.01329 | 1 | 0.00041 | 0.0038 | 0.00113 | 0.00233 | 0.01329
345 | 795.0 26/7 ACSR DRAKE | 1 | 7#8 | DBL ckt | 933 | 557.5212 | 0.00012 | 0.00068 | 0.0063 | 0.0005 | 0.0018 | 1 | 0.00012 | 0.00068 | 0.0063 | 0.0005 | 0.0018
345 | 795.0 26/7 ACSR DRAKE | 1 | OPGW | DBL ckt | 933 | 557.5212 | 0.00012 | 0.00068 | 0.00631 | 0.00031 | 0.00153 | 1 | 0.00012 | 0.00068 | 0.00631 | 0.00031 | 0.00153
345 | 795.0 26/7 ACSR DRAKE | 1 | 7#8 | SINGLE ckt | 933 | 557.5212 | 0.00012 | 0.00068 | 0.00627 | 0.00046 | 0.00195 | 1 | 0.00012 | 0.00068 | 0.00627 | 0.00046 | 0.00195
345 | 795.0 26/7 ACSR DRAKE | 1 | OPGW | SINGLE ckt | 933 | 557.5212 | 0.00012 | 0.00068 | 0.00627 | 0.00035 | 0.0017 | 1 | 0.00012 | 0.00068 | 0.00627 | 0.00035 | 0.0017
138 | 959.6 22/7 ACSS/ TW SUWANNEE | 2 | OPGW | H | 3190 | 762.4834 | 0.0003 | 0.00275 | 0.00156 | 0.00178 | 0.0072 | 3.8 | 0.00114 | 0.01045 | 0.005928 | 0.006764 | 0.02736
138 | 959.6 22/7 ACSS/ TW SUWANNEE | 2 | OPGW | DBL ckt | 3190 | 762.4834 | 0.0003 | 0.00273 | 0.00158 | 0.00163 | 0.00812 | 9.5 | 0.00285 | 0.025935 | 0.01501 | 0.015485 | 0.07714
138 | 959.6 22/7 ACSS/ TW SUWANNEE | 2 | OPGW | delta | 3190 | 762.4834 | 0.0003 | 0.00284 | 0.00149 | 0.00192 | 0.00918 | 9.5 | 0.00285 | 0.02698 | 0.014155 | 0.01824 | 0.08721
138 | 959.6 22/7 ACSS/ TW SUWANNEE | 2 | OPGW | vertical | 3190 | 762.4834 | 0.0003 | 0.00273 | 0.00157 | 0.00193 | 0.00931 | 3.62 | 0.001086 | 0.0098826 | 0.0056834 | 0.0069866 | 0.033702
138 | 959.6 22/7 ACSS/ TW SUWANNEE | 2 | 7#8 | H | 3190 | 762.4834 | 0.0003 | 0.00276 | 0.00155 | 0.00341 | 0.00984 | 1 | 0.0003 | 0.00276 | 0.00155 | 0.00341 | 0.00984
138 | 959.6 22/7 ACSS/ TW SUWANNEE | 2 | 7#8 | DBL ckt | 3190 | 762.4834 | 0.0003 | 0.00274 | 0.00158 | 0.00308 | 0.01023 | 1 | 0.0003 | 0.00274 | 0.00158 | 0.00308 | 0.01023
138 | 959.6 22/7 ACSS/ TW SUWANNEE | 2 | 7#8 | delta | 3190 | 762.4834 | 0.0003 | 0.00284 | 0.00149 | 0.00273 | 0.01119 | 1 | 0.0003 | 0.00284 | 0.00149 | 0.00273 | 0.01119
138 | 959.6 22/7 ACSS/ TW SUWANNEE | 2 | 7#8 | vertical | 3190 | 762.4834 | 0.0003 | 0.00274 | 0.00157 | 0.00276 | 0.01137 | 1 | 0.0003 | 0.00274 | 0.00157 | 0.00276 | 0.01137
138 | 959.6 22/7 ACSS/ TW SUWANNEE | 2 | 3/8 | H | 3190 | 762.4834 | 0.0003 | 0.00276 | 0.00156 | 0.00276 | 0.0116 | 1 | 0.0003 | 0.00276 | 0.00156 | 0.00276 | 0.0116
138 | 959.6 22/7 ACSS/ TW SUWANNEE | 2 | 3/8 | DBL ckt | 3190 | 762.4834 | 0.0003 | 0.00274 | 0.00158 | 0.00258 | 0.01176 | 1 | 0.0003 | 0.00274 | 0.00158 | 0.00258 | 0.01176
138 | 959.6 22/7 ACSS/ TW SUWANNEE | 2 | 3/8 | delta | 3190 | 762.4834 | 0.0003 | 0.00284 | 0.00149 | 0.00222 | 0.01203 | 1 | 0.0003 | 0.00284 | 0.00149 | 0.00222 | 0.01203
138 | 959.6 22/7 ACSS/ TW SUWANNEE | 2 | 3/8 | vertical | 3190 | 762.4834 | 0.0003 | 0.00274 | 0.00157 | 0.00223 | 0.01223 | 1 | 0.0003 | 0.00274 | 0.00157 | 0.00223 | 0.01223
345 | 1590.0 45/7 ACSR LAPWING | 1 | 7#8 | DBL ckt | 1370.3349 | 818.854 | 6e-05 | 0.00065 | 0.00662 | 0.00044 | 0.00178 | 1 | 6e-05 | 0.00065 | 0.00662 | 0.00044 | 0.00178
345 | 1590.0 45/7 ACSR LAPWING | 1 | OPGW | DBL ckt | 1370.3349 | 818.854 | 6e-05 | 0.00065 | 0.00662 | 0.00026 | 0.00152 | 1 | 6e-05 | 0.00065 | 0.00662 | 0.00026 | 0.00152
345 | 1590.0 45/7 ACSR LAPWING | 1 | 7#8 | SINGLE ckt | 1370.3349 | 818.854 | 6e-05 | 0.00065 | 0.00658 | 0.0004 | 0.00192 | 1 | 6e-05 | 0.00065 | 0.00658 | 0.0004 | 0.00192
345 | 1590.0 45/7 ACSR LAPWING | 1 | OPGW | SINGLE ckt | 1370.3349 | 818.854 | 6e-05 | 0.00065 | 0.00659 | 0.00029 | 0.00168 | 1 | 6e-05 | 0.00065 | 0.00659 | 0.00029 | 0.00168
345 | 959.6 22/7 ACSS/ TW SUWANNEE | 1 | 7#8 | DBL ckt | 1595 | 953.1043 | 0.0001 | 0.00068 | 0.0063 | 0.00048 | 0.00181 | 1 | 0.0001 | 0.00068 | 0.0063 | 0.00048 | 0.00181
345 | 959.6 22/7 ACSS/ TW SUWANNEE | 1 | OPGW | DBL ckt | 1595 | 953.1043 | 0.0001 | 0.00068 | 0.00631 | 0.00029 | 0.00153 | 9.5 | 0.00095 | 0.00646 | 0.059945 | 0.002755 | 0.014535
345 | 959.6 22/7 ACSS/ TW SUWANNEE | 1 | 7#8 | SINGLE ckt | 1595 | 953.1043 | 0.0001 | 0.00068 | 0.00627 | 0.00044 | 0.00195 | 1 | 0.0001 | 0.00068 | 0.00627 | 0.00044 | 0.00195
345 | 959.6 22/7 ACSS/ TW SUWANNEE | 1 | OPGW | SINGLE ckt | 1595 | 953.1043 | 0.0001 | 0.00068 | 0.00627 | 0.00033 | 0.0017 | 9.5 | 0.00095 | 0.00646 | 0.059565 | 0.003135 | 0.01615
138 | 1433.6 39/19 ACSS/TW MERRIMACK | 2 | OPGW | H | 4000 | 956.092 | 0.00021 | 0.00269 | 0.00159 | 0.00167 | 0.00726 | 9.5 | 0.001995 | 0.025555 | 0.015105 | 0.015865 | 0.06897
138 | 1433.6 39/19 ACSS/TW MERRIMACK | 2 | OPGW | DBL ckt | 4000 | 956.092 | 0.00021 | 0.00267 | 0.00162 | 0.00152 | 0.00815 | 9.5 | 0.001995 | 0.025365 | 0.01539 | 0.01444 | 0.077425
138 | 1433.6 39/19 ACSS/TW MERRIMACK | 2 | OPGW | delta | 4000 | 956.092 | 0.0002 | 0.00278 | 0.00152 | 0.00181 | 0.00918 | 9.5 | 0.0019 | 0.02641 | 0.01444 | 0.017195 | 0.08721
138 | 1433.6 39/19 ACSS/TW MERRIMACK | 2 | OPGW | vertical | 4000 | 956.092 | 0.00021 | 0.00267 | 0.00161 | 0.00183 | 0.00932 | 9.5 | 0.001995 | 0.025365 | 0.015295 | 0.017385 | 0.08854
138 | 1433.6 39/19 ACSS/TW MERRIMACK | 2 | 7#8 | H | 4000 | 956.092 | 0.0002 | 0.0027 | 0.00159 | 0.00328 | 0.00983 | 1 | 0.0002 | 0.0027 | 0.00159 | 0.00328 | 0.00983
138 | 1433.6 39/19 ACSS/TW MERRIMACK | 2 | 7#8 | DBL ckt | 4000 | 956.092 | 0.00021 | 0.00268 | 0.00162 | 0.00296 | 0.01021 | 1 | 0.00021 | 0.00268 | 0.00162 | 0.00296 | 0.01021
138 | 1433.6 39/19 ACSS/TW MERRIMACK | 2 | 7#8 | delta | 4000 | 956.092 | 0.0002 | 0.00278 | 0.00152 | 0.00262 | 0.01114 | 1 | 0.0002 | 0.00278 | 0.00152 | 0.00262 | 0.01114
138 | 1433.6 39/19 ACSS/TW MERRIMACK | 2 | 7#8 | vertical | 4000 | 956.092 | 0.00021 | 0.00268 | 0.00161 | 0.00264 | 0.01133 | 1 | 0.00021 | 0.00268 | 0.00161 | 0.00264 | 0.01133
138 | 1433.6 39/19 ACSS/TW MERRIMACK | 2 | 3/8 | H | 4000 | 956.092 | 0.0002 | 0.0027 | 0.00159 | 0.00264 | 0.01155 | 1 | 0.0002 | 0.0027 | 0.00159 | 0.00264 | 0.01155
138 | 1433.6 39/19 ACSS/TW MERRIMACK | 2 | 3/8 | DBL ckt | 4000 | 956.092 | 0.00021 | 0.00268 | 0.00162 | 0.00247 | 0.01171 | 1 | 0.00021 | 0.00268 | 0.00162 | 0.00247 | 0.01171
138 | 1433.6 39/19 ACSS/TW MERRIMACK | 2 | 3/8 | delta | 4000 | 956.092 | 0.0002 | 0.00279 | 0.00152 | 0.00212 | 0.01198 | 1 | 0.0002 | 0.00279 | 0.00152 | 0.00212 | 0.01198
138 | 1433.6 39/19 ACSS/TW MERRIMACK | 2 | 3/8 | vertical | 4000 | 956.092 | 0.0002 | 0.00268 | 0.00161 | 0.00213 | 0.01218 | 1 | 0.0002 | 0.00268 | 0.00161 | 0.00213 | 0.01218
345 | 795.0 26/7 ACSR DRAKE | 2 | 7#8 | DBL ckt | 1866 | 1115.0423 | 6e-05 | 0.00049 | 0.0087 | 0.00045 | 0.00162 | 1 | 6e-05 | 0.00049 | 0.0087 | 0.00045 | 0.00162
345 | 795.0 26/7 ACSR DRAKE | 2 | OPGW | DBL ckt | 1866 | 1115.0423 | 6e-05 | 0.00049 | 0.00871 | 0.00025 | 0.00135 | 1 | 6e-05 | 0.00049 | 0.00871 | 0.00025 | 0.00135
345 | 795.0 26/7 ACSR DRAKE | 2 | 7#8 | SINGLE ckt | 1866 | 1115.0423 | 6e-05 | 0.00049 | 0.00863 | 0.0004 | 0.00176 | 1 | 6e-05 | 0.00049 | 0.00863 | 0.0004 | 0.00176
345 | 795.0 26/7 ACSR DRAKE | 2 | OPGW | SINGLE ckt | 1866 | 1115.0423 | 6e-05 | 0.00049 | 0.00864 | 0.00029 | 0.00151 | 1 | 6e-05 | 0.00049 | 0.00864 | 0.00029 | 0.00151
345 | 1433.6 39/19 ACSS/TW MERRIMACK | 1 | 7#8 | DBL ckt | 2000 | 1195.1151 | 7e-05 | 0.00066 | 0.00649 | 0.00045 | 0.00179 | 1 | 7e-05 | 0.00066 | 0.00649 | 0.00045 | 0.00179
345 | 1433.6 39/19 ACSS/TW MERRIMACK | 1 | OPGW | DBL ckt | 2000 | 1195.1151 | 7e-05 | 0.00066 | 0.0065 | 0.00026 | 0.00153 | 1 | 7e-05 | 0.00066 | 0.0065 | 0.00026 | 0.00153
345 | 1433.6 39/19 ACSS/TW MERRIMACK | 1 | 7#8 | SINGLE ckt | 2000 | 1195.1151 | 7e-05 | 0.00066 | 0.00646 | 0.00041 | 0.00193 | 1 | 7e-05 | 0.00066 | 0.00646 | 0.00041 | 0.00193
345 | 1433.6 39/19 ACSS/TW MERRIMACK | 1 | OPGW | SINGLE ckt | 2000 | 1195.1151 | 7e-05 | 0.00066 | 0.00646 | 0.0003 | 0.00169 | 1 | 7e-05 | 0.00066 | 0.00646 | 0.0003 | 0.00169
345 | 1926.9 42/19 ACSS/TW CUMBERLAND | 1 | 7#8 | DBL ckt | 2500 | 1493.8938 | 5e-05 | 0.00065 | 0.00665 | 0.00043 | 0.00178 | 1 | 5e-05 | 0.00065 | 0.00665 | 0.00043 | 0.00178
345 | 1926.9 42/19 ACSS/TW CUMBERLAND | 1 | OPGW | DBL ckt | 2500 | 1493.8938 | 5e-05 | 0.00065 | 0.00665 | 0.00024 | 0.00151 | 1 | 5e-05 | 0.00065 | 0.00665 | 0.00024 | 0.00151
345 | 1926.9 42/19 ACSS/TW CUMBERLAND | 1 | 7#8 | SINGLE ckt | 2500 | 1493.8938 | 5e-05 | 0.00065 | 0.00661 | 0.00039 | 0.00192 | 1 | 5e-05 | 0.00065 | 0.00661 | 0.00039 | 0.00192
345 | 1926.9 42/19 ACSS/TW CUMBERLAND | 1 | OPGW | SINGLE ckt | 2500 | 1493.8938 | 5e-05 | 0.00065 | 0.00662 | 0.00028 | 0.00167 | 1 | 5e-05 | 0.00065 | 0.00662 | 0.00028 | 0.00167
345 | 1590.0 45/7 ACSR LAPWING | 2 | 7#8 | DBL ckt | 2740.6699 | 1637.7079 | 3e-05 | 0.00048 | 0.009 | 0.00041 | 0.00161 | 1 | 3e-05 | 0.00048 | 0.009 | 0.00041 | 0.00161
345 | 1590.0 45/7 ACSR LAPWING | 2 | OPGW | DBL ckt | 2740.6699 | 1637.7079 | 3e-05 | 0.00048 | 0.00901 | 0.00022 | 0.00135 | 1 | 3e-05 | 0.00048 | 0.00901 | 0.00022 | 0.00135
345 | 1590.0 45/7 ACSR LAPWING | 2 | 7#8 | SINGLE ckt | 2740.6699 | 1637.7079 | 3e-05 | 0.00048 | 0.00892 | 0.00037 | 0.00175 | 1 | 3e-05 | 0.00048 | 0.00892 | 0.00037 | 0.00175
345 | 1590.0 45/7 ACSR LAPWING | 2 | OPGW | SINGLE ckt | 2740.6699 | 1637.7079 | 3e-05 | 0.00048 | 0.00893 | 0.00026 | 0.00151 | 1 | 3e-05 | 0.00048 | 0.00893 | 0.00026 | 0.00151
345 | 959.6 22/7 ACSS/ TW SUWANNEE | 2 | 7#8 | DBL ckt | 3190 | 1906.2085 | 5e-05 | 0.00049 | 0.0087 | 0.00043 | 0.00162 | 1 | 5e-05 | 0.00049 | 0.0087 | 0.00043 | 0.00162
345 | 959.6 22/7 ACSS/ TW SUWANNEE | 2 | OPGW | DBL ckt | 3190 | 1906.2085 | 5e-05 | 0.00049 | 0.00871 | 0.00024 | 0.00135 | 9.5 | 0.000475 | 0.004655 | 0.082745 | 0.00228 | 0.012825
345 | 959.6 22/7 ACSS/ TW SUWANNEE | 2 | 7#8 | SINGLE ckt | 3190 | 1906.2085 | 5e-05 | 0.00049 | 0.00863 | 0.00039 | 0.00176 | 1 | 5e-05 | 0.00049 | 0.00863 | 0.00039 | 0.00176
345 | 959.6 22/7 ACSS/ TW SUWANNEE | 2 | OPGW | SINGLE ckt | 3190 | 1906.2085 | 5e-05 | 0.00049 | 0.00864 | 0.00028 | 0.00151 | 9.5 | 0.000475 | 0.004655 | 0.08208 | 0.00266 | 0.014345
345 | 1433.6 39/19 ACSS/TW MERRIMACK | 2 | 7#8 | DBL ckt | 4000 | 2390.2301 | 3e-05 | 0.00048 | 0.00889 | 0.00042 | 0.00161 | 1 | 3e-05 | 0.00048 | 0.00889 | 0.00042 | 0.00161
345 | 1433.6 39/19 ACSS/TW MERRIMACK | 2 | OPGW | DBL ckt | 4000 | 2390.2301 | 3e-05 | 0.00048 | 0.00889 | 0.00023 | 0.00135 | 1 | 3e-05 | 0.00048 | 0.00889 | 0.00023 | 0.00135
345 | 1433.6 39/19 ACSS/TW MERRIMACK | 2 | 7#8 | SINGLE ckt | 4000 | 2390.2301 | 3e-05 | 0.00048 | 0.00881 | 0.00037 | 0.00175 | 1 | 3e-05 | 0.00048 | 0.00881 | 0.00037 | 0.00175
345 | 1433.6 39/19 ACSS/TW MERRIMACK | 2 | OPGW | SINGLE ckt | 4000 | 2390.2301 | 3e-05 | 0.00048 | 0.00882 | 0.00026 | 0.00151 | 1 | 3e-05 | 0.00048 | 0.00882 | 0.00026 | 0.00151
345 | 1926.9 42/19 ACSS/TW CUMBERLAND | 2 | 7#8 | DBL ckt | 5000 | 2987.7876 | 3e-05 | 0.00048 | 0.00903 | 0.00041 | 0.00161 | 1 | 3e-05 | 0.00048 | 0.00903 | 0.00041 | 0.00161
345 | 1926.9 42/19 ACSS/TW CUMBERLAND | 2 | OPGW | DBL ckt | 5000 | 2987.7876 | 3e-05 | 0.00048 | 0.00904 | 0.00022 | 0.00134 | 1 | 3e-05 | 0.00048 | 0.00904 | 0.00022 | 0.00134
345 | 1926.9 42/19 ACSS/TW CUMBERLAND | 2 | 7#8 | SINGLE ckt | 5000 | 2987.7876 | 3e-05 | 0.00048 | 0.00895 | 0.00037 | 0.00175 | 1 | 3e-05 | 0.00048 | 0.00895 | 0.00037 | 0.00175
345 | 1926.9 42/19 ACSS/TW CUMBERLAND | 2 | OPGW | SINGLE ckt | 5000 | 2987.7876 | 3e-05 | 0.00048 | 0.00896 | 0.00026 | 0.0015 | 1 | 3e-05 | 0.00048 | 0.00896 | 0.00026 | 0.0015
Note on C1: Kristian Koellner: Select 2 if bundled.
Note on D1: Kristian Koellner: Assume OPGW if unknown.
Note on E1: Kristian Koellner: Assume delta if unknown.
Note on F1: Kristian Koellner: Based on LCRA TSC Transmission System Planning Criteria Table 1 values.
Note on M1: Kristian Koellner: Enter miles for your planned line in column M.

## Instructions
1 | Select the conductor characteristics which match your project using the Excel filters in row 1.
2 | If you are not sure about the shield wire, assume OPGW (more projects may begin to include OPGW going forward).
3 | If you are not sure about the geometry, assume delta (provides the lowest X0 value among commonly used configurations).
4 | Note: The two values above mostly only impact the zero sequence quantities.
5 | Enter the mileage for your planned line in column M.
6 | The impedance values for the planned line are contained in columns N through R.
7 | Be sure to capture zero sequence values for inclusion in the short circuit cases and the Planned tab of the Impedance Report
8 | For any questions, please contact Sharron, Gene, Ross, or Kris.

## Assumptions
These line impedance values are provided by System Protection for use in assessing alternatives related to Planning studies
The impedance of a representative 1 mile line has been estimated for varying conductor, structure, shield wire, etc designs.
Selected parameters include:
Conductors per phase
1
2
Geometry incl. vertical offset
H
Double circuit
Vertical
Delta
Conductor
1433.6 39/19 ACSS/TW MERRIMACK
1590.0 45/7 ACSR LAPWING
1926.9 42/19 ACSS/TW CUMBERLAND
336.4 26/7 ACSR LINNET
477.0 26/7 ACSR HAWK
795.0 26/7 ACSR DRAKE
795.0 26/7 ACSS/TW DRAKE
959.6 22/7 ACSS/ TW SUWANNEE
Shield
OPGW
3/8" steel
7#8 Alumoweld
Voltage
69-kV
138-kV
345-kV
Assumptions common to each line impedance estimate include:
69-kV & 138-kV vertical offset: 50 feet
345-kV vertical offset: 95 feet
18 inch vertical bundling
69-kV and 138-kV ruling span: 700 feet
345-kV ruling span: 1,000 feet
Shield conductor temp: 25 deg C
Phase conductor temp: 75 deg C
Soil resistivity: 125 ohm-meters
Dual OPGW assumed for double circuit configuration

## Original (hidden)
kV | Conductor | Conductors Per Phase | Miles | Limiting Amps | MVA | R / Mile | X / Mile | B / Mile | R0 / Mile | X0 / Mile | ENTER MILES HERE | R | X | B | R0 | X0
69 | 1/0 6/1 ACSR RAVEN | 1 | 1 | 256.3975 | 30.6425 | 0.021869 | 0.018879 | 0.00024485 | 0.031442 | 0.058123 | 1 | 0.021869 | 0.018879 | 0.00024485 | 0.031442 | 0.058123
69 | 1433.6 39/19 ACSS/TW MERRIMACK | 1 | 1 | 2062.3171 | 246.4706 | 0.0014955 | 0.014156 | 0.00030048 | 0.011068 | 0.053399 | 1 | 0.0014955 | 0.014156 | 0.00030048 | 0.011068 | 0.053399
138 | 1433.6 39/19 ACSS/TW MERRIMACK | 1 | 1 | 2062.3171 | 492.9412 | 0.00037387 | 0.0037305 | 0.0011379 | 0.0025929 | 0.013062 | 1 | 0.00037387 | 0.0037305 | 0.0011379 | 0.0025929 | 0.013062
138 | 1433.6 39/19 ACSS/TW MERRIMACK | 2 | 1 | 4124.6341 | 985.8825 | 0.00018694 | 0.0026142 | 0.0016064 | 0.0012964 | 0.013062 | 1 | 0.00018694 | 0.0026142 | 0.0016064 | 0.0012964 | 0.013062
345 | 1433.6 39/19 ACSS/TW MERRIMACK | 2 | 1 | 4124.6341 | 2464.7062 | 2.991e-05 | 0.00048238 | 0.0086746 | 0.0002298 | 0.0018954 | 1 | 2.991e-05 | 0.00048238 | 0.0086746 | 0.0002298 | 0.0018954
69 | 1590.0 45/7 ACSR LAPWING | 1 | 1 | 1370.3349 | 163.7708 | 0.0014094 | 0.01391 | 0.00030707 | 0.010982 | 0.053153 | 1 | 0.0014094 | 0.01391 | 0.00030707 | 0.010982 | 0.053153
138 | 1590.0 45/7 ACSR LAPWING | 1 | 1 | 1370.3349 | 327.5416 | 0.00035234 | 0.0036691 | 0.0011615 | 0.0025713 | 0.013 | 1 | 0.00035234 | 0.0036691 | 0.0011615 | 0.0025713 | 0.013
138 | 1590.0 45/7 ACSR LAPWING | 2 | 1 | 2740.6699 | 655.0832 | 0.00017617 | 0.0025835 | 0.0016297 | 0.0012857 | 0.013 | 1 | 0.00017617 | 0.0025835 | 0.0016297 | 0.0012857 | 0.013
345 | 1590.0 45/7 ACSR LAPWING | 2 | 1 | 2740.6699 | 1637.7079 | 2.8187e-05 | 0.00047747 | 0.0087835 | 0.00022808 | 0.0018856 | 1 | 2.8187e-05 | 0.00047747 | 0.0087835 | 0.00022808 | 0.0018856
69 | 336.4 26/7 ACSR LINNET | 1 | 1 | 533.8113 | 63.7966 | 0.0062928 | 0.015731 | 0.00026937 | 0.015866 | 0.054974 | 1 | 0.0062928 | 0.015731 | 0.00026937 | 0.015866 | 0.054974
138 | 336.4 26/7 ACSR LINNET | 1 | 1 | 533.8113 | 127.5932 | 0.0015732 | 0.0041244 | 0.0010257 | 0.0037922 | 0.013455 | 1 | 0.0015732 | 0.0041244 | 0.0010257 | 0.0037922 | 0.013455
138 | 336.4 26/7 ACSR LINNET | 2 | 1 | 1067.6226 | 255.1864 | 0.0007866 | 0.0028111 | 0.0014913 | 0.0018961 | 0.013455 | 1 | 0.0007866 | 0.0028111 | 0.0014913 | 0.0018961 | 0.013455
345 | 336.4 26/7 ACSR LINNET | 2 | 1 | 1067.6226 | 637.9659 | 0.00012586 | 0.00051389 | 0.0081323 | 0.00032575 | 0.0019584 | 1 | 0.00012586 | 0.00051389 | 0.0081323 | 0.00032575 | 0.0019584
69 | 4/0 6/1 ACSR PENGUIN | 1 | 1 | 396.1198 | 47.3409 | 0.011821 | 0.017216 | 0.00025869 | 0.021394 | 0.056459 | 1 | 0.011821 | 0.017216 | 0.00025869 | 0.021394 | 0.056459
138 | 4/0 6/1 ACSR PENGUIN | 1 | 1 | 396.1198 | 94.6818 | 0.0029553 | 0.0044956 | 0.0009869 | 0.0051743 | 0.013827 | 1 | 0.0029553 | 0.0044956 | 0.0009869 | 0.0051743 | 0.013827
138 | 4/0 6/1 ACSR PENGUIN | 2 | 1 | 792.2396 | 189.3635 | 0.0014776 | 0.0029967 | 0.0014498 | 0.0025871 | 0.013827 | 1 | 0.0014776 | 0.0029967 | 0.0014498 | 0.0025871 | 0.013827
345 | 4/0 6/1 ACSR PENGUIN | 2 | 1 | 792.2396 | 473.4088 | 0.00023642 | 0.00054359 | 0.0079345 | 0.00043631 | 0.0020178 | 1 | 0.00023642 | 0.00054359 | 0.0079345 | 0.00043631 | 0.0020178
69 | 477.0 26/7 ACSR HAWK | 1 | 1 | 665.9166 | 79.5847 | 0.0044591 | 0.015286 | 0.00027721 | 0.014032 | 0.054529 | 1 | 0.0044591 | 0.015286 | 0.00027721 | 0.014032 | 0.054529
138 | 477.0 26/7 ACSR HAWK | 1 | 1 | 665.9166 | 159.1694 | 0.0011148 | 0.004013 | 0.0010541 | 0.0033338 | 0.013344 | 1 | 0.0011148 | 0.004013 | 0.0010541 | 0.0033338 | 0.013344
138 | 477.0 26/7 ACSR HAWK | 2 | 1 | 1331.8332 | 318.3388 | 0.00055739 | 0.0027554 | 0.001521 | 0.0016669 | 0.013344 | 1 | 0.00055739 | 0.0027554 | 0.001521 | 0.0016669 | 0.013344
345 | 477.0 26/7 ACSR HAWK | 2 | 1 | 1331.8332 | 795.847 | 8.9183e-05 | 0.00050498 | 0.0082737 | 0.00028908 | 0.0019406 | 1 | 8.9183e-05 | 0.00050498 | 0.0082737 | 0.00028908 | 0.0019406
69 | 795.0 26/7 ACSR DRAKE | 1 | 1 | 920.2376 | 109.979 | 0.0026843 | 0.014639 | 0.00029005 | 0.012257 | 0.053882 | 1 | 0.0026843 | 0.014639 | 0.00029005 | 0.012257 | 0.053882
138 | 795.0 26/7 ACSR DRAKE | 1 | 1 | 920.2376 | 219.958 | 0.00067108 | 0.0038513 | 0.0011004 | 0.0028901 | 0.013182 | 1 | 0.00067108 | 0.0038513 | 0.0011004 | 0.0028901 | 0.013182
138 | 795.0 26/7 ACSR DRAKE | 2 | 1 | 1840.4751 | 439.9159 | 0.00033554 | 0.0026746 | 0.0015687 | 0.001445 | 0.013182 | 1 | 0.00033554 | 0.0026746 | 0.0015687 | 0.001445 | 0.013182
345 | 795.0 26/7 ACSR DRAKE | 2 | 1 | 1840.4751 | 1099.7898 | 5.3686e-05 | 0.00049204 | 0.0084981 | 0.00025358 | 0.0019147 | 1 | 5.3686e-05 | 0.00049204 | 0.0084981 | 0.00025358 | 0.0019147
69 | 959.6 22/7 ACSS/ TW SUWANNEE | 1 | 1 | 1639.237 | 195.9077 | 0.0021718 | 0.014639 | 0.00029005 | 0.011745 | 0.053882 | 1 | 0.0021718 | 0.014639 | 0.00029005 | 0.011745 | 0.053882
138 | 959.6 22/7 ACSS/ TW SUWANNEE | 1 | 1 | 1639.237 | 391.8154 | 0.00054295 | 0.0038513 | 0.0011004 | 0.0027619 | 0.013182 | 1 | 0.00054295 | 0.0038513 | 0.0011004 | 0.0027619 | 0.013182
138 | 959.6 22/7 ACSS/ TW SUWANNEE | 2 | 1 | 3278.4739 | 783.6307 | 0.00027148 | 0.0026746 | 0.0015687 | 0.001381 | 0.013182 | 1 | 0.00027148 | 0.0026746 | 0.0015687 | 0.001381 | 0.013182
345 | 959.6 22/7 ACSS/ TW SUWANNEE | 2 | 1 | 3278.4739 | 1959.0768 | 4.3436e-05 | 0.00049204 | 0.0084981 | 0.00024333 | 0.0019147 | 1 | 4.3436e-05 | 0.00049204 | 0.0084981 | 0.00024333 | 0.0019147

## Comparison (hidden)
kV | Conductor | Conductors Per Phase | Miles | Shield | Geometry | Amps | MVA | R / Mile | X / Mile | B / Mile | R0 / Mile | X0 / Mile | kV | Conductor | Conductors Per Phase | Miles | Limiting Amps | MVA | R / Mile | X / Mile | B / Mile | R0 / Mile | X0 / Mile | R / Mile | X / Mile | B / Mile | R0 / Mile | X0 / Mile
138 | 1433.6 39/19 ACSS/TW MERRIMACK | 1 | 1 | 7#8 | delta | 2062.3171 | 492.9412 | 0.00041 | 0.0039 | 0.0011 | 0.00282 | 0.01226 | 138 | 1433.6 39/19 ACSS/TW MERRIMACK | 1 | 1 | 2062.3171 | 492.9412 | 0.00037387 | 0.0037305 | 0.0011379 | 0.0025929 | 0.013062 | 109.7% | 104.5% | 96.67% | 108.8% | 93.86%
138 | 1433.6 39/19 ACSS/TW MERRIMACK | 2 | 1 | 7#8 | delta | 4124.6341 | 985.8825 | 0.0002 | 0.00278 | 0.00152 | 0.00262 | 0.01114 | 138 | 1433.6 39/19 ACSS/TW MERRIMACK | 2 | 1 | 4124.6341 | 985.8825 | 0.00018694 | 0.0026142 | 0.0016064 | 0.0012964 | 0.013062 | 107% | 106.3% | 94.62% | 202.1% | 85.29%
345 | 1433.6 39/19 ACSS/TW MERRIMACK | 1 | 1 | 7#8 | SINGLE ckt | 2062.3171 | 1232.3531 | 7e-05 | 0.00066 | 0.00646 | 0.00041 | 0.00193
345 | 1433.6 39/19 ACSS/TW MERRIMACK | 2 | 1 | 7#8 | SINGLE ckt | 4124.6341 | 2464.7062 | 3e-05 | 0.00048 | 0.00881 | 0.00037 | 0.00175 | 345 | 1433.6 39/19 ACSS/TW MERRIMACK | 2 | 1 | 4124.6341 | 2464.7062 | 2.991e-05 | 0.00048238 | 0.0086746 | 0.0002298 | 0.0018954 | 100.3% | 99.51% | 101.6% | 161% | 92.33%
345 | 1590.0 45/7 ACSR LAPWING | 1 | 1 | 7#8 | SINGLE ckt | 1370.3349 | 818.854 | 6e-05 | 0.00065 | 0.00658 | 0.0004 | 0.00192
345 | 1590.0 45/7 ACSR LAPWING | 2 | 1 | 7#8 | SINGLE ckt | 2740.6699 | 1637.7079 | 3e-05 | 0.00048 | 0.00892 | 0.00037 | 0.00175 | 345 | 1590.0 45/7 ACSR LAPWING | 2 | 1 | 2740.6699 | 1637.7079 | 2.8187e-05 | 0.00047747 | 0.0087835 | 0.00022808 | 0.0018856 | 106.4% | 100.5% | 101.6% | 162.2% | 92.81%
345 | 1926.9 42/19 ACSS/TW CUMBERLAND | 1 | 1 | 7#8 | SINGLE ckt |  |  | 5e-05 | 0.00065 | 0.00661 | 0.00039 | 0.00192
345 | 1926.9 42/19 ACSS/TW CUMBERLAND | 2 | 1 | 7#8 | SINGLE ckt |  |  | 3e-05 | 0.00048 | 0.00895 | 0.00037 | 0.00175
69 | 336.4 26/7 ACSR LINNET | 1 | 1 | 7#8 | delta | 533.8113 | 63.7966 | 0.00687 | 0.01717 | 0.00025 | 0.01664 | 0.05052 | 69 | 336.4 26/7 ACSR LINNET | 1 | 1 | 533.8113 | 63.7966 | 0.0062928 | 0.015731 | 0.00026937 | 0.015866 | 0.054974 | 109.2% | 109.1% | 92.81% | 104.9% | 91.9%
138 | 477.0 26/7 ACSR HAWK | 1 | 1 | 7#8 | delta | 665.9166 | 159.1694 | 0.00121 | 0.00418 | 0.00102 | 0.00365 | 0.01253 | 138 | 477.0 26/7 ACSR HAWK | 1 | 1 | 665.9166 | 159.1694 | 0.0011148 | 0.004013 | 0.0010541 | 0.0033338 | 0.013344 | 108.5% | 104.2% | 96.77% | 109.5% | 93.9%
138 | 477.0 26/7 ACSR HAWK | 2 | 1 | 7#8 | delta | 1331.8332 | 318.3388 | 0.00061 | 0.00292 | 0.00145 | 0.00304 | 0.01127 | 138 | 477.0 26/7 ACSR HAWK | 2 | 1 | 1331.8332 | 318.3388 | 0.00055739 | 0.0027554 | 0.001521 | 0.0016669 | 0.013344 | 109.4% | 106% | 95.33% | 182.4% | 84.46%
69 | 795.0 26/7 ACSR DRAKE | 1 | 1 | 7#8 | delta | 920.2376 | 109.979 | 0.00293 | 0.01607 | 0.00027 | 0.01267 | 0.04945 | 69 | 795.0 26/7 ACSR DRAKE | 1 | 1 | 920.2376 | 109.979 | 0.0026843 | 0.014639 | 0.00029005 | 0.012257 | 0.053882 | 109.2% | 109.8% | 93.09% | 103.4% | 91.77%
138 | 795.0 26/7 ACSR DRAKE | 1 | 1 | 7#8 | delta | 920.2376 | 219.958 | 0.00073 | 0.00402 | 0.00106 | 0.00317 | 0.01236 | 138 | 795.0 26/7 ACSR DRAKE | 1 | 1 | 920.2376 | 219.958 | 0.00067108 | 0.0038513 | 0.0011004 | 0.0028901 | 0.013182 | 108.8% | 104.4% | 96.33% | 109.7% | 93.76%
138 | 795.0 26/7 ACSR DRAKE | 2 | 1 | 7#8 | delta | 1840.4751 | 439.9159 | 0.00037 | 0.00284 | 0.00149 | 0.0028 | 0.01119 | 138 | 795.0 26/7 ACSR DRAKE | 2 | 1 | 1840.4751 | 439.9159 | 0.00033554 | 0.0026746 | 0.0015687 | 0.001445 | 0.013182 | 110.3% | 106.2% | 94.99% | 193.8% | 84.89%
345 | 795.0 26/7 ACSR DRAKE | 1 | 1 | 7#8 | SINGLE ckt | 920.2376 | 549.8949 | 0.00012 | 0.00068 | 0.00627 | 0.00046 | 0.00195
345 | 795.0 26/7 ACSR DRAKE | 2 | 1 | 7#8 | SINGLE ckt | 1840.4751 | 1099.7898 | 6e-05 | 0.00049 | 0.00863 | 0.0004 | 0.00176 | 345 | 795.0 26/7 ACSR DRAKE | 2 | 1 | 1840.4751 | 1099.7898 | 5.3686e-05 | 0.00049204 | 0.0084981 | 0.00025358 | 0.0019147 | 111.8% | 99.58% | 101.6% | 157.7% | 91.92%
138 | 795.0 26/7 ACSS/TW DRAKE | 1 | 1 | 7#8 | delta |  |  | 0.00072 | 0.00402 | 0.00106 | 0.00316 | 0.01235
138 | 795.0 26/7 ACSS/TW DRAKE | 2 | 1 | 7#8 | delta |  |  | 0.00036 | 0.00284 | 0.00149 | 0.0028 | 0.01118
138 | 959.6 22/7 ACSS/ TW SUWANNEE | 1 | 1 | 7#8 | delta | 1639.237 | 391.8154 | 0.00059 | 0.00402 | 0.00106 | 0.00303 | 0.01236 | 138 | 959.6 22/7 ACSS/ TW SUWANNEE | 1 | 1 | 1639.237 | 391.8154 | 0.00054295 | 0.0038513 | 0.0011004 | 0.0027619 | 0.013182 | 108.7% | 104.4% | 96.33% | 109.7% | 93.76%
138 | 959.6 22/7 ACSS/ TW SUWANNEE | 2 | 1 | 7#8 | delta | 3278.4739 | 783.6307 | 0.0003 | 0.00284 | 0.00149 | 0.00273 | 0.01119 | 138 | 959.6 22/7 ACSS/ TW SUWANNEE | 2 | 1 | 3278.4739 | 783.6307 | 0.00027148 | 0.0026746 | 0.0015687 | 0.001381 | 0.013182 | 110.5% | 106.2% | 94.99% | 197.7% | 84.89%
345 | 959.6 22/7 ACSS/ TW SUWANNEE | 1 | 1 | 7#8 | SINGLE ckt | 3278.4739 | 1959.0768 | 0.0001 | 0.00068 | 0.00627 | 0.00044 | 0.00195
345 | 959.6 22/7 ACSS/ TW SUWANNEE | 2 | 1 | 7#8 | SINGLE ckt | 3278.4739 | 1959.0768 | 5e-05 | 0.00049 | 0.00863 | 0.00039 | 0.00176 | 345 | 959.6 22/7 ACSS/ TW SUWANNEE | 2 | 1 | 3278.4739 | 1959.0768 | 4.3436e-05 | 0.00049204 | 0.0084981 | 0.00024333 | 0.0019147 | 115.1% | 99.58% | 101.6% | 160.3% | 91.92%
Note on G24: Kristian M. Koellner: Update with TS criteria values to be updated by TLD/TP. Add column for conductor temp.

## EST VS ACTUAL (hidden)
ERCOT ID | kV | Ckt | From | From Bus | To | To Bus | R1 | X1 | B1 | R0 | X0 | Length
ACTUAL HORIZ. BUNDLED CUMBERLAND DC W/OPGW AND 7#8 ALUM
224T558 | 345 | 558 | 60709 | ORSTED7B | 60616 | EDISON7A | 0.0013301 | 0.025021 | 0.47901 | 0.014829 | 0.075488 | 52.799
FOR ESTIMATE USED VERT. BUNDLED CUMBERLAND W/OPGW | [6 empty] | 0.001584 | 0.025344 | 0.47731 | 0.011616 | 0.070752 | 52.8
ACTUAL 1/2 H AND 1/2 VERT 795 ACSR DRAKE W/2 3/8 ON THE H STR AND 1-3/8 ON THE VERT
| 138 | 260 | 7310 | GIDEON13 | 7324 | BUTLER13 | 0.020724 | 0.1108 | 0.031255 | 0.081177 | 0.35729 | 28.374
FOR ESTIMATE USED 1/2 H AND 1/2 VERT 795 ACSR DRAKE W/2 3/8 ON THE H STR AND 1-3/8 ON THE VERT
[6 empty] | H | 0.010366 | 0.055806 | 0.015478 | 0.045298 | 0.18133 | 14.2
[6 empty] | VERT | 0.010366 | 0.055664 | 0.01562 | 0.037914 | 0.19028 | 14.2
[7 empty] | 0.020732 | 0.11147 | 0.031098 | 0.083212 | 0.37161 | 28.4
ACTUAL VERT. DRAKE ACSR W/3/8 AND OPGW
| 69 | 540 | 78581 | L_MAGNTA9_1Y | 78584 | L_HELENA9_1 | 0.01988 | 0.10332 | 0.0019071 | 0.063028 | 0.27996 | 6.773
FOR ESTIMATE USED VERT DRAKE ACSR AND OPGW | [6 empty] | 0.019992 | 0.10635 | 0.001836 | 0.064328 | 0.28526 | 6.8